AB   Axis Industries

Heat meter SKS-3

M-bus communication protocol description

2012

Table of contents

|  | # 1. Reading of integral and moment parameters ……………………………………….. | 3 |
| --- | --- | --- |
|  | # 2. Readout of hours and days archive ………………………………………………….. | 6 |
|  | # 3. Secondary addressing ……………………………………………………………….. | 11 |
|  | # 4. Reading the relay output parameters ………………………………………………… | 12 |
|  | # 5. Setting the relay output parameters ………………………………………………….. | 13 |
|  | 6. Reading of meter configuration ………………………………………………………. | 13 |

# 1. Reading of integral and moment parameters

First is SND_NKE / E5 negotiation is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 40h | A | CS | 16h |

Answer of the meter:

0

E5h

A – M-bus primary address

CS – control sum

Then the selection of integral and moment parameters is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 04h | 04h | 68h | 53h | A | 50h | 00h | CS | 16h |

Answer of the meter:

0

E5h

Then the query for data is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 5B/7B | A | CS | 16 |

Answer of the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | L | L | 68h | 08h | A | 72h | Nr0 | Nr1 | Nr2 | Nr3 | 09h | 07h | 03h | 04h |

| 15 | 16 | 17 | 18 | 19-(n-2) | n-1 | n |
| --- | --- | --- | --- | --- | --- | --- |
| Acc | 00h | 00h | 00h | Integral and moment parameters block | CS | 16h |

7...10  bytes:  „Nr0... Nr3“ – Serial number of meter,

11, 12 bytes:   „09h,07h“ – Manufacturer code  (AXI)

13 byte:  „03h“ – Number of  M-bus protocol version (3)

14 byte:  „04h“ –  Measured  medium („Heat“)

In the block of integral moment parameters can be following parameters (depending on configuration of the meter):

- Energy 1  (for 1st heating system, except scheme U0).

- Energy 2  (for 2nd  heating system, except scheme U0).

- Energy 3  (for 1st heating system for schemes A1, A2 and A4).

- Volume (or mass) 1 (when flow input 1  is active).

- Volume (or mass) 2 1 (when  flow input 2 is active).

- Volume (or mass) -2 (when  flow input 2 is active, A1 scheme and algorythm 3 is selected).

- Volume (or mass) 3 (when  flow input 3 is active).

- Volume (or mass) 4 (when  flow input 4 is active).

- Volume 5 (when  flow input 5 is active).

- Power 1 (except scheme U0).

- Power 2 (except scheme U0).

- Power 3 (for 1st heating system for schemes A1, A2 and A4).

- Flow 1 (when flow input 1  is active).

- Flow 2 ((when flow input 2  is active).

- Flow 3 (when flow input 3  is active).

- Flow 4 (when flow input 4  is active).

- Flow 5 (when flow input 5  is active).

- Temperature 1 (when temperature input 1  is active).

- Temperature 2 (when temperature input 2  is active).

- Temperature 3 (when temperature input 3  is active).

- Temperature 4 (when temperature input 4  is active).

- Temperature 5 (when temperature input 5  is active).

- Pressure 1  (when pressure input 1  is active).

- Pressure 2  (when pressure input 2  is active).

Also, independently of configuration, following parameters are in the block:

- Current date/time of the meter

- Error codes

- Power supply duration

- Normal working time

- Additional control sum (CRC-16)

Coding of parameters:

## Energy

| Parameter | DIB | VIB |  |  |  |  |  |  |  | Data |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 0,1 MWh | 0,1 GJ | 0,01 MWh | 0,01 GJ | 0,001 MWh | 0,001 GJ | 0,0001 MWh | 0,0001 GJ |  |
| 1st energy | 04 | FB 00 | FB 08 | 07 | 0F | 06 | 0E | 05 | 0D | 4 bytes (long) |
| 2nd energy | 84 40 | FB 00 | FB 08 | 07 | 0F | 06 | 0E | 05 | 0D | 4 bytes (long) |
| 3d energy | 84 80 40 | FB 00 | FB 08 | 07 | 0F | 06 | 0E | 05 | 0D | 4 bytes (long) |

## Volume (or mass)

| Parameter | DIB | VIB |  |  |  |  |  |  |  | Data |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 m3 | 1 t | 0,1 m3 | 0,1 t | 0,01 m3 | 0,01 t | 0,001 m3 | 0,001 t |  |
| Volume (mass) 1 | 04 | 16 | 96 | 15 | 95 | 14 | 94 | 13 | 93 | 4 bytes (long) |
| Volume (mass) 2 | 84 40 | 16 | 96 | 15 | 95 | 14 | 94 | 13 | 93 | 4 bytes (long) |
| Volume (mass) 3 | 84 80 40 | 16 | 96 | 15 | 95 | 14 | 94 | 13 | 93 | 4 bytes (long) |
| Volume (mass) 4 | 84 C0 40 | 16 | 96 | 15 | 95 | 14 | 94 | 13 | 93 | 4 bytes (long) |
| Volume (mass) 5 | 84 80 80 40 | 16 | 96 | 15 | 95 | 14 | 94 | 13 | 93 | 4 bytes (long) |
| Volume (mass) -2 | 84 C0 80 40 | 16 | 96 | 15 | 95 | 14 | 94 | 13 | 93 | 4 bytes (long) |

## Power

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Power 1 | 05 | 2E | 4 bytes (float) kW |
| Power 2 | 85 40 | 2E | 4 bytes (float) kW |
| Power 3 | 85 80 40 | 2E | 4 bytes (float) kW |

## Flow

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Flow 1 | 05 | 3E | 4 bytes (float) m3/h |
| Flow 2 | 85 40 | 3E | 4 bytes (float) m3/h |
| Flow 3 | 85 80 40 | 3E | 4 bytes (float) m3/h |
| Flow 4 | 85 C0 40 | 3E | 4 bytes (float) m3/h |
| Flow 5 | 85 80 80 40 | 3E | 4 bytes (float) m3/h |

## Temperature

| Parametras | DIB | VIB | Data |
| --- | --- | --- | --- |
| Temperature 1 | 02 | 59 | 2 bytes (word), 0,01oC |
| Temperature 2 | 02 | 5D | 2 bytes (word), 0,01oC |
| Temperature 3 | 82 40 | 59 | 2 bytes (word), 0,01oC |
| Temperature 4 | 82 40 | 5D | 2 bytes (word), 0,01oC |
| Temperature 5 | 02 | 65 | 2 bytes (word), 0,01oC |

## Pressure

| Parametras | DIB | VIB | Data |
| --- | --- | --- | --- |
| Pressure 1 | 03 | 68 | 3 bytes (word) 0,1 kPa |
| Pressure 1 | 83 40 | 68 | 3 bytes (word) 0,1 kPa |

## Current date/time

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Date/time | 44 | 6D | 4 bytes (date/time format) |

Format of date/time is following:

| Bytes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 3 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |
| Bits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 31 | 30 | 29 | 28 | 27 | 26 | 25 | 24 | 23 | 22 | 21 | 20 | 19 | 18 | 17 | 16 | 15 | 14 | 13 | 12 | 11 | 10 | 09 | 08 | 07 | 06 | 05 | 04 | 03 | 02 | 01 | 00 |
| Year1 |  |  |  | Month |  |  |  | Year0 |  |  | Day |  |  |  |  | 0 | 0 | 0 | Hour |  |  |  |  | 0 | 0 | Minutes |  |  |  |  |  |

Minutes - <0 to 59>

Hour - <0 to 23>

Day - <1 to 31>

Month - <1 to 12>

Year=Year1|Year0 (Year0 – low significant part, Year1 – high significant part) <0 to 99>

## Error codes

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Error code Er∑ | 02 | FD 17 | 2 bytes (error code format) |
| Error code Er1 | 82 40 | FD 17 | 2 bytes (error code format) |
| Error code Er2 | 82 80 40 | FD 17 | 2 bytes (error code format) |

Format of error code Er∑  is following:

| Bytes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |
| Bits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 | 14 | 13 | 12 | 11 | 10 | 09 | 08 | 07 | 06 | 05 | 04 | 03 | 02 | 01 | 00 |
| Bits of error code |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3 | 2 | 1 | 0 | 3 | 2 | 1 | 0 | 3 | 2 | 1 | 0 |
| Not used (=0) |  |  |  | Calculator operation error code |  |  |  | 2nd heating system operation error code |  |  |  | 1st heating system operation error code |  |  |  |

Format of error code Er1  is following:

| Bytes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |
| Bits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 | 14 | 13 | 12 | 11 | 10 | 09 | 08 | 07 | 06 | 05 | 04 | 03 | 02 | 01 | 00 |
| Bits of error code |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 3 | 2 | 1 | 3 | 2 | 1 | 3 | 2 | 1 | 3 | 2 | 1 | 3 | 2 | 1 |
| 0 | Status code of flow sensor 5 |  |  | Status code of flow sensor 4 |  |  | Status code of flow sensor 3 |  |  | Status code of flow sensor 2 |  |  | Status code of flow sensor 1 |  |  |

Format of error code Er2  is following:

| Bytes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |
| Bits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 | 14 | 13 | 12 | 11 | 10 | 09 | 08 | 07 | 06 | 05 | 04 | 03 | 02 | 01 | 00 |
| Bits of error code |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 3 | 1 | 0 | 3 | 1 | 0 | 3 | 1 | 0 | 3 | 1 | 0 | 3 | 1 | 0 |
| 0 | Status code of tem- perature sensor 5 |  |  | Status code of tem- perature sensor 4 |  |  | Status code of tem- perature sensor 3 |  |  | Status code of tem- perature sensor 2 |  |  | Status code of tem- perature sensor 1 |  |  |

## Power supply duration

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Power supply duration | 04 | 20 | 4 bytes (long integer, time in seconds) |

## Normal working time

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| For 1st heating system | 04 | 24 | 4 bytes (long integer, time in seconds) |
| For 2nd heating system | 84 40 | 24 | 4 bytes (long integer, time in seconds) |

## Additional control sum (CRC-16)

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Additional control sum (CRC-16) | 02 | 7F | 2 bytes |

# 2. Readout of hours and days archive

First is SND_NKE / E5 negotiation is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 40h | A | CS | 16h |

Answer of the meter:

0

E5h

Selection of hours or days archive is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 04h | 04h | 68h | 53h | A | 50h | 04h – for hours archive 03h – for days archive | CS | 16h |

Answer of the meter:

0

E5h

Then the query for data is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 5B/7B | A | CS | 16 |

Answer of the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | L | L | 68h | 08h | A | 72h | Nr0 | Nr1 | Nr2 | Nr3 | 34h | 2Ch | 03h | 04h |

| 15 | 16 | 17 | 18 | 19-(n-2) | n-1 | n |
| --- | --- | --- | --- | --- | --- | --- |
| Acc | 00h | 00h | 00h | Hours/days archive record block | CS | 16h |

The readout of the next record of the archive is performed by sending data query packet with changed 1st byte 5Bh/7Bh (toggling the most significant bit of the byte). Archive readout is performed from the newest records.

In the first block of hours and days archive can be following parameters (depending on meter configuration):

- Energy 1  (for 1st heating system, except scheme U0).

- Energy 2  (for 2nd  heating system, except scheme U0).

- Energy 3  (for 1st heating system for schemes A1, A2 and A4).

- Volume (or mass) 1 (when flow input 1  is active).

- Volume (or mass) 2 1 (when  flow input 2 is active).

- Volume (or mass) -2 (when  flow input 2 is active, A1 scheme and algorythm 3 is selected).

- Volume (or mass) 3 (when  flow input 3 is active).

- Volume (or mass) 4 (when  flow input 4 is active).

- Volume 5 (when  flow input 5 is active).

- Power 1 (except scheme U0).

- Power 2 (except scheme U0).

- Power 3 (for 1st heating system for schemes A1, A2 and A4).

- Flow 1 (when flow input 1  is active).

- Flow 2 ((when flow input 2  is active).

- Flow 3 (when flow input 3  is active).

- Flow 4 (when flow input 4  is active).

- Flow 5 (when flow input 5  is active).

- Temperature 1 (when temperature input 1  is active).

- Temperature 2 (when temperature input 2  is active).

- Temperature 3 (when temperature input 3  is active).

- Temperature 4 (when temperature input 4  is active).

- Temperature 5 (when temperature input 5  is active).

- Pressure 1  (when pressure input 1  is active).

- Pressure 2  (when pressure input 2  is active).

Also, independently of configuration, following parameters are in the block:

- Current date/time of the meter

- Error codes

- Power supply duration

- Normal working time

- Additional control sum (CRC-16)

In second  block can be following parameters (depending on meter configuration):

- Duration of failure (failure in 1st  and/or 2nd  heating system)

- 1st heating system failure duration.

- 2nd  heating system failure duration.

- Duration, when flow q1 > q1max.

- Duration, when flow q2 > q2max.

- Duration, when flow q3 > q3max.

- Duration, when flow q4 > q4max.

- Duration, when flow q1 < q1min.

- Duration, when flow q2 < q2min.

- Duration, when flow q3 < q3min.

- Duration, when flow q4 < q4min.

- Duration, when temperature difference  (T1-T2) < (T1-T2)min.

- Duration, when temperature difference  (T3-T4) < (T3-T4)min.

Coding of parameters:

## Energy

| Parameter | DIB | VIB |  |  |  |  |  |  |  | Data |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 0,1 MWh | 0,1 GJ | 0,01 MWh | 0,01 GJ | 0,001 MWh | 0,001 GJ | 0,0001 MWh | 0,0001 GJ |  |
| 1st energy | 04 | FB 00 | FB 08 | 07 | 0F | 06 | 0E | 05 | 0D | 4 bytes (long) |
| 2nd energy | 84 40 | FB 00 | FB 08 | 07 | 0F | 06 | 0E | 05 | 0D | 4 bytes (long) |
| 3d energy | 84 80 40 | FB 00 | FB 08 | 07 | 0F | 06 | 0E | 05 | 0D | 4 bytes (long) |

## Volume (or mass)

| Parameter | DIB | VIB |  |  |  |  |  |  |  | Data |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 m3 | 1 t | 0,1 m3 | 0,1 t | 0,01 m3 | 0,01 t | 0,001 m3 | 0,001 t |  |
| Volume (mass) 1 | 04 | 16 | 96 | 15 | 95 | 14 | 94 | 13 | 93 | 4 bytes (long) |
| Volume (mass) 2 | 84 40 | 16 | 96 | 15 | 95 | 14 | 94 | 13 | 93 | 4 bytes (long) |
| Volume (mass) 3 | 84 80 40 | 16 | 96 | 15 | 95 | 14 | 94 | 13 | 93 | 4 bytes (long) |
| Volume (mass) 4 | 84 C0 40 | 16 | 96 | 15 | 95 | 14 | 94 | 13 | 93 | 4 bytes (long) |
| Volume (mass) 5 | 84 80 80 40 | 16 | 96 | 15 | 95 | 14 | 94 | 13 | 93 | 4 bytes (long) |
| Volume (mass) -2 | 84 C0 80 40 | 16 | 96 | 15 | 95 | 14 | 94 | 13 | 93 | 4 bytes (long) |

## Temperature (average)

| Parametras | DIB | VIB | Data |
| --- | --- | --- | --- |
| Temperature 1 | 02 | 59 | 2 bytes (word), 0,01oC |
| Temperature 2 | 02 | 5D | 2 bytes (word), 0,01oC |
| Temperature 3 | 82 40 | 59 | 2 bytes (word), 0,01oC |
| Temperature 4 | 82 40 | 5D | 2 bytes (word), 0,01oC |
| Temperature 5 | 02 | 65 | 2 bytes (word), 0,01oC |

## Pressure (average)

| Parametras | DIB | VIB | Data |
| --- | --- | --- | --- |
| Pressure 1 | 03 | 68 | 3 bytes (word) 0,1 kPa |
| Pressure 1 | 83 40 | 68 | 3 bytes (word) 0,1 kPa |

## Date and time of records

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Date/time | 44 | 6D | 4 bytes (date/time format) |

Format of date/time is following:

| Bytes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 3 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |
| Bits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 31 | 30 | 29 | 28 | 27 | 26 | 25 | 24 | 23 | 22 | 21 | 20 | 19 | 18 | 17 | 16 | 15 | 14 | 13 | 12 | 11 | 10 | 09 | 08 | 07 | 06 | 05 | 04 | 03 | 02 | 01 | 00 |
| Year1 |  |  |  | Month |  |  |  | Year0 |  |  | Day |  |  |  |  | 0 | 0 | 0 | Hour |  |  |  |  | 0 | 0 | Minutes |  |  |  |  |  |

Minutes - <0 to 59>

Hour - <0 to 23>

Day - <1 to 31>

Month - <1 to 12>

Year=Year1|Year0 (Year0 – low significant part, Year1 – high significant part) <0 to 99>

## Error codes

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Error code Er∑ | 02 | FD 17 | 2 bytes (error code format) |
| Error code Er1 | 82 40 | FD 17 | 2 bytes (error code format) |
| Error code Er2 | 82 80 40 | FD 17 | 2 bytes (error code format) |

Format of error code Er∑  is following:

| Bytes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |
| Bits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 | 14 | 13 | 12 | 11 | 10 | 09 | 08 | 07 | 06 | 05 | 04 | 03 | 02 | 01 | 00 |
| Bits of error code |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3 | 2 | 1 | 0 | 3 | 2 | 1 | 0 | 3 | 2 | 1 | 0 |
| Not used (=0) |  |  |  | Calculator operation error code |  |  |  | 2nd heating system operation error code |  |  |  | 1st heating system operation error code |  |  |  |

Format of error code Er1  is following:

| Bytes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |
| Bits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 | 14 | 13 | 12 | 11 | 10 | 09 | 08 | 07 | 06 | 05 | 04 | 03 | 02 | 01 | 00 |
| Bits of error code |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 3 | 2 | 1 | 3 | 2 | 1 | 3 | 2 | 1 | 3 | 2 | 1 | 3 | 2 | 1 |
| 0 | Status code of flow sensor 5 |  |  | Status code of flow sensor 4 |  |  | Status code of flow sensor 3 |  |  | Status code of flow sensor 2 |  |  | Status code of flow sensor 1 |  |  |

Format of error code Er2  is following:

| Bytes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |
| Bits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 | 14 | 13 | 12 | 11 | 10 | 09 | 08 | 07 | 06 | 05 | 04 | 03 | 02 | 01 | 00 |
| Bits of error code |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 3 | 1 | 0 | 3 | 1 | 0 | 3 | 1 | 0 | 3 | 1 | 0 | 3 | 1 | 0 |
| 0 | Status code of tem- perature sensor 5 |  |  | Status code of tem- perature sensor 4 |  |  | Status code of tem- perature sensor 3 |  |  | Status code of tem- perature sensor 2 |  |  | Status code of tem- perature sensor 1 |  |  |

## Power on duration

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Power on duration | 04 | 20 | 4 bytes (long integer, time in seconds) |

## Power supply duration

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Power supply duration | 04 | 20 | 4 bytes (long integer, time in seconds) |

## Normal working time

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| For 1st heating system | 04 | 24 | 4 bytes (long integer, time in seconds) |
| For 2nd heating system | 84 40 | 24 | 4 bytes (long integer, time in seconds) |

## Additional control sum (CRC-16)

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Additional control sum (CRC-16) | 02 | 7F | 2 bytes |

## Duration of  errors

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Duration of failure (failure in 1st and/or 2nd heating system) | 04 | 74 | 4 bytes (long integer, time in seconds) |
| 1st heating system failure duration | 84 40 | 74 | 4 bytes (long integer, time in seconds) |
| 2nd heating system failure duration | 84 80 40 | 74 | 4 bytes (long integer, time in seconds) |
| Duration, when flow q1 > q1max | 84 C0 40 | 74 | 4 bytes (long integer, time in seconds) |
| Duration, when flow q2 > q2max | 84 80 80 40 | 74 | 4 bytes (long integer, time in seconds) |
| Duration, when flow q3 > q3max | 84 C0 80 40 | 74 | 4 bytes (long integer, time in seconds) |
| Duration, when flow q4 > q4max | 84 80 C0 40 | 74 | 4 bytes (long integer, time in seconds) |
| Duration, when flow q1 < q1min | 84 C0 C0 40 | 74 | 4 bytes (long integer, time in seconds) |
| Duration, when flow q2 < q2min | 84 80 80 80 40 | 74 | 4 bytes (long integer, time in seconds) |
| Duration, when flow q3 < q3min | 84 C0 80 80 40 | 74 | 4 bytes (long integer, time in seconds) |
| Duration, when flow q4 < q4min | 84 80 C0 80 40 | 74 | 4 bytes (long integer, time in seconds) |
| Duration, when temperature difference (T1-T2) < (T1-T2)min | 84 C0 C0 80 40 | 74 | 4 bytes (long integer, time in seconds) |
| Duration, when temperature difference (T3-T4) < (T3-T4)min | 84 80 80 C0 40 | 74 | 4 bytes (long integer, time in seconds) |

# 3. Secondary addressing

Meter supports secondary addressing. The address of secondary addressing is meter parameter “Serial number” (Nr), and most significant digit (7-th) of address splits meter in to 1 … 9 sub-meters.

Possible meter response telegrams, depending on the address code,   secondary address type meter configuration code bits (B0. .. B9) and meter configuration, see on the table:

| Adress | Transmitted data | Conditions |
| --- | --- | --- |
| {Nr} | As primary addressing case (see chapter 1) | B0=1 (or all B0,B1…B7=0) (standard settings) |
| {Nr} | Transmitted parameters E∑, ton, coded as E, ton | When code over than „B1=1 and B0,B2…B7=0“ and E∑ is on |
| {Nr} | Transmitted parameters E1, V1(or M1), P1, q1, T1, T2, T5, p1, p2, ton, td1, coded as E, V(or M), P, q, T1, T2, Ts, p1, p2, ton, td | When B1=1 and B0,B2…B7=0, and 1st heating scheme no U2 or A2 |
| {Nr} | Transmitted parameters E1, V2(or M2), P1, q1, T1, T2, T5, p1, p2, ton, td1, coded as E, V(or M), P, q, T1, T2, Ts, p1, p2, ton, td | When B1=1 and B0,B2…B7=0, and 1st heating scheme U2 or A2 |
| {1000000+Nr} | Transmitted parameters E1, V1(or M1), P1, q1, T1, T2, T5, p1, p2, ton, td1, coded as E, V(or M), P, q, T1, T2, Ts, p1, p2, ton, td | B1=1 and 1st flow channel is on, and 1st heating scheme no U2 or A2 |
| {1000000+Nr} | Transmitted parameters E1, V2(or M2), P1, q1, T1, T2, T5, p1, p2, ton, td1, coded as E, V(or M), P, q, T1, T2, Ts, p1, p2, ton, td | B1=1 and 2nd flow channel is on, and 1st heating scheme U2 or A2 |
| {2000000+Nr} | Transmitted parameters E2, V3(or M3), P2, q3, T3, T4, p1, p2, ton, td2, coded as E, V(or M), P, q, T1, T2, p1, p2, ton, td | B2=1 and 3d flow channel is on, and 2nd heating scheme no U2 |
| {2000000+Nr} | Transmitted parameters E2, V3(or M3), P2, q3, T1, T2, p1, p2, ton, td2, coded as E, V(or M), P, q, T1, T2, p1, p2, ton, td | B2=1 and 4th flow channel is on, and 2nd heating scheme U2 |
| {3000000+Nr} | Transmitted parameters V2(or M2), q2, coded as V (or M), q | B3=1 and 2nd flow channel is on, and 1st heating scheme no U2 |
| {3000000+Nr} | Transmitted parameters V1(or M1), q1, coded as V (or M), q | B3=1 and 1st flow channel is on, and 1st heating scheme U2 |
| {4000000+Nr} | Transmitted parameters V4(or M4), q4, coded as V (or M), q | B4=1 and 4th flow channel is on, and 2nd heating scheme no U2 |
| {4000000+Nr} | Transmitted parameters V3(or M3), q3, coded as V (or M), q | B4=1 and 3d flow channel is on, and 2nd heating scheme U2 |
| {5000000+Nr} | Transmitted parameters V5, q5, coded as V, q | B5=1 and 5th flow channel is on |
| {6000000+Nr} | Days archive | B6=1 |
| {7000000+Nr} | Hours archive | B7=1 |
| {8000000+Nr} | Days archive from end of last month | B8=1 |
| {9000000+Nr} | Hours archive from end of last month | B9=1 |

Here: 	E – energy   ( total energy E∑  = E1 + E2)

V – volume  (M – mass)

P – power

q – flow

T – temperature

p – pressure

ton – power supply duration

td– normal working time

1…5 – number of channel (or heating system)

## 4. Reading the relay output parameters

First is SND_NKE / E5 negotiation is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 40h | A | CS | 16h |

Answer of the meter:

0

E5h

Selection of relay output parameters is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 04h | 04h | 68h | 53h | A | 50h | 05h | CS | 16h |

Answer of the meter:

0

E5h

Then the query for data is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 5B/7B | A | CS | 16 |

Answer of the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 21h | 21h | 68h | 08h | A | 72h | Nr0 | Nr1 | Nr2 | Nr3 | 34h | 2Ch | 04h | 04h |

| 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Acc | 00h | 00h | 00h | 0Fh | 00h | RelP | 00h | Max0 | Max1 | Max2 | Max3 | Min0 | Min1 | Min2 | Min3 |

| 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RegT0 | RegT1 | RegL0 | RegL1 | RegCS0 | RegCS1 | CS | 16 |

Parameters:

| Parameter | Description |
| --- | --- |
| RelP | Code of parameter for relay output |
| Max | Upper value limit of regulated parameter (float) |
| Min | Lower value limit of regulated parameter (float) |
| RegT | Integral constant for regulation time (integer, sec) |
| RegL | Regulated valve run time (integer, sec) |
| Reg CS | Control sum of parameters RelP...RegL |

## 5. Setting the relay output parameters

Master sends following packet to the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 15h | 15h | 68h | 53h | A | 51h | 0Fh | 00h | RelP | 00h | Max0 | Max1 | Max2 | Max3 |

| 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Min0 | Min1 | Min2 | Min3 | RegT0 | RegT1 | RegL0 | RegL1 | RegCS0 | RegCS1 | CS | 16 |

Answer of the meter:

0

E5h

Parameters:

| Parameter | Description |
| --- | --- |
| RelP | Code of parameter for relay output |
| Max | Upper value limit of regulated parameter (float) |
| Min | Lower value limit of regulated parameter (float) |
| RegT | Integral constant for regulation time (integer, sec) |
| RegL | Regulated valve run time (integer, sec) |
| Reg CS | Control sum of parameters RelP...RegL |

# 6. Reading of meter configuration

First is SND_NKE / E5 negotiation is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 40h | A | CS | 16h |

Answer of the meter:

0

E5h

Then the selection of configuration parameters is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | n-1 | n |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 04h | 04h | 68h | 53h | A | 50h | 06h | CS | 16h |

Answer of the meter:

0

E5h

Then the query for data is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 5B/7B | A | CS | 16 |

Answer of the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | L | L | 68h | 08h | A | 72h | Nr0 | Nr1 | Nr2 | Nr3 | 34h | 2Ch | 03h | 04h |

| 15 | 16 | 17 | 18 | 19 | 20 | 21-(n-2) | n-1 | n |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Acc | 00h | 00h | 00h | 0Fh | 01h | Configuration of the meter | CS | 16 |

| Offset in bytes | Parameter (format) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 0 | Nr0 | Serial number (Unsigned integer) |  |  |  |
| 1 | Nr1 |  |  |  |  |
| 2 | Nr2 |  |  |  |  |
| 3 | Nr3 |  |  |  |  |
| 4 | ANr0 | Customer number (Unsigned integer) |  |  |  |
| 5 | ANr1 |  |  |  |  |
| 6 | ANr2 |  |  |  |  |
| 7 | ANr3 |  |  |  |  |
| 8 | BatData0 | Battery change date (Unsigned integer, seconds since 2004.01.01 00:00) |  |  |  |
| 9 | BatData1 |  |  |  |  |
| 10 | BatData02 |  |  |  |  |
| 11 | BatData03 |  |  |  |  |
| 12 | Modif1 | Code of scheme of 1st system: 0x00 – U0 0x01 – U1 0x02 – U2 0x03 – U3 0x04 – A1 0x05 – A2 0x06 – A3 0x07 – A4 |  |  |  |
| 13 | Alg1 | Code of algorithm of 1st system |  |  |  |
| 14 | Modif2 | Code of scheme of 2nd system: 0x00 – U0 0x01 – U1 0x02 – U2 0x03 – U3 |  |  |  |
| 15 | Alg2 | Code of algorithm of 2nd system |  |  |  |
| 16 | DSAR | List of active flow inputs Bits. 7; 6; 5; 4; 3; 2; 1; 0. 0; 0; 0; q5; q4; q3; q2; q1. |
| 17 | TSAR | List of active temperature inputs Bits. 7; 6; 5; 4; 3; 2; 1; 0. 0; 0; 0; T5; T4; T3; T2; T1. |
| 18 | SSAR | List of active pressure inputs Bits. 7; 6; 5; 4; 3; 2; 1; 0. 0; 0; 0; 0; 0; 0; p2; p1. |
| 19 | TGRAD1 | Code off temperature sensor 1 type |  | 0x00 – PT500 0x01 – PT1000 0x02 – 500П 0x03 – 1000П |  |
| 20 | TGRAD2 | Code off temperature sensor 2 type |  |  |  |
| 21 | TGRAD3 | Code off temperature sensor 3 type |  |  |  |
| 22 | TGRAD4 | Code off temperature sensor 4 type |  |  |  |
| 23 | TGRAD5 | Code off temperature sensor 5 type |  |  |  |
| 24 | DTIP1 | Flow sensor 1 type |  |  |  |
| 25 | DIM1 | Units of flow measuring channel 1: 0x00 – m3 0x01 – t |  |  |  |
| 26 | DADF10 | Minimal pulse period of flow input 1 (integer, msec) |  |  |  |
| 27 | DADF11 |  |  |  |  |
| 28 | DTIP2 | Flow sensor 2 type |  |  |  |
| 29 | DIM2 | Units of flow measuring channel 2: 0x00 – m3 0x01 – t |  |  |  |
| 30 | DADF20 | Minimal pulse period of flow input 2 (integer, msec) |  |  |  |
| 31 | DADF21 |  |  |  |  |
| 32 | DTIP3 | Flow sensor 3 type |  |  |  |
| 33 | DIM3 | Units of flow measuring channel 3: 0x00 – m3 0x01 – t |  |  |  |
| 34 | DADF30 | Minimal pulse period of flow input 3 (integer, msec) |  |  |  |
| 35 | DADF31 |  |  |  |  |
| 36 | DTIP4 | Flow sensor 4 type |  |  |  |
| 37 | DIM4 | Units of flow measuring channel 4: 0x00 – m3 0x01 – t |  |  |  |
| 38 | DADF40 | Minimal pulse period of flow input 4 (integer, msec) |  |  |  |
| 39 | DADF41 |  |  |  |  |
| 40 | DTIP5 | Flow sensor 5 type (visada 0x00) |  |  |  |
| 41 | DIM5 | Not used (0x00) |  |  |  |
| 42 | DADF50 | Minimal pulse period of flow input 5 (integer, msec) |  |  |  |
| 43 | DADF51 |  |  |  |  |
| 44 | DIMP10 | Pulse value of flow input 1 (float, m3/pulse) |  |  |  |
| 45 | DIMP11 |  |  |  |  |
| 46 | DIMP12 |  |  |  |  |
| 47 | DIMP13 |  |  |  |  |
| 48 | DIMP20 | Pulse value of flow input 2 (float, m3/pulse) |  |  |  |
| 49 | DIMP21 |  |  |  |  |
| 50 | DIMP22 |  |  |  |  |
| 51 | DIMP23 |  |  |  |  |
| 52 | DIMP30 | Pulse value of flow input 3 (float, m3/pulse) |  |  |  |
| 53 | DIMP31 |  |  |  |  |
| 54 | DIMP32 |  |  |  |  |
| 55 | DIMP33 |  |  |  |  |
| 56 | DIMP40 | Pulse value of flow input 4 (float, m3/pulse) |  |  |  |
| 57 | DIMP41 |  |  |  |  |
| 58 | DIMP42 |  |  |  |  |
| 59 | DIMP43 |  |  |  |  |
| 60 | DIMP50 | Pulse value of flow input 5 (float, m3/pulse) |  |  |  |
| 61 | DIMP51 |  |  |  |  |
| 62 | DIMP52 |  |  |  |  |
| 63 | DIMP53 |  |  |  |  |
| 64 | QMAX10 | Max flow of flow input 1 (float, m3/h) |  |  |  |
| 65 | QMAX11 |  |  |  |  |
| 66 | QMAX12 |  |  |  |  |
| 67 | QMAX13 |  |  |  |  |
| 68 | QMAX20 | Max flow of flow input 2 (float, m3/h) |  |  |  |
| 69 | QMAX21 |  |  |  |  |
| 70 | QMAX22 |  |  |  |  |
| 71 | QMAX23 |  |  |  |  |
| 72 | QMAX30 | Max flow of flow input 3 (float, m3/h) |  |  |  |
| 73 | QMAX31 |  |  |  |  |
| 74 | QMAX32 |  |  |  |  |
| 75 | QMAX33 |  |  |  |  |
| 76 | QMAX40 | Max flow of flow input 4 (float, m3/h) |  |  |  |
| 77 | QMAX41 |  |  |  |  |
| 78 | QMAX42 |  |  |  |  |
| 79 | QMAX43 |  |  |  |  |
| 80 | QMAX50 | Max flow of flow input 5 (float, m3/h) |  |  |  |
| 81 | QMAX51 |  |  |  |  |
| 82 | QMAX52 |  |  |  |  |
| 83 | QMAX53 |  |  |  |  |
| 84 | QMIN10 | Min flow of flow input 1 (float, m3/h) |  |  |  |
| 85 | QMIN11 |  |  |  |  |
| 86 | QMIN12 |  |  |  |  |
| 87 | QMIN13 |  |  |  |  |
| 88 | QMIN20 | Min flow of flow input 2 (float, m3/h) |  |  |  |
| 89 | QMIN21 |  |  |  |  |
| 90 | QMIN22 |  |  |  |  |
| 91 | QMIN23 |  |  |  |  |
| 92 | QMIN30 | Min flow of flow input 3 (float, m3/h) |  |  |  |
| 93 | QMIN31 |  |  |  |  |
| 94 | QMIN32 |  |  |  |  |
| 95 | QMIN33 |  |  |  |  |
| 96 | QMIN40 | Min flow of flow input 4 (float, m3/h) |  |  |  |
| 97 | QMIN41 |  |  |  |  |
| 98 | QMIN42 |  |  |  |  |
| 99 | QMIN43 |  |  |  |  |
| 100 | QPMAX10 | Max projected value of flow of flow input 1 (float, m3/h) |  |  |  |
| 101 | QPMAX11 |  |  |  |  |
| 102 | QPMAX12 |  |  |  |  |
| 103 | QPMAX13 |  |  |  |  |
| 104 | QPMAX20 | Max projected value of flow of flow input 2 (float, m3/h) |  |  |  |
| 105 | QPMAX21 |  |  |  |  |
| 106 | QPMAX22 |  |  |  |  |
| 107 | QPMAX23 |  |  |  |  |
| 108 | QPMAX30 | Max projected value of flow of flow input 3 (float, m3/h) |  |  |  |
| 109 | QPMAX31 |  |  |  |  |
| 110 | QPMAX32 |  |  |  |  |
| 111 | QPMAX33 |  |  |  |  |
| 112 | QPMAX40 | Max projected value of flow of flow input 4 (float, m3/h) |  |  |  |
| 113 | QPMAX41 |  |  |  |  |
| 114 | QPMAX42 |  |  |  |  |
| 115 | QPMAX43 |  |  |  |  |
| 116 | QPMIN10 | Min projected value of flow of flow input 1 (float, m3/h) |  |  |  |
| 117 | QPMIN11 |  |  |  |  |
| 118 | QPMIN12 |  |  |  |  |
| 119 | QPMIN13 |  |  |  |  |
| 120 | QPMIN20 | Min projected value of flow of flow input 2 (float, m3/h) |  |  |  |
| 121 | QPMIN21 |  |  |  |  |
| 122 | QPMIN22 |  |  |  |  |
| 123 | QPMIN23 |  |  |  |  |
| 124 | QPMIN30 | Min projected value of flow of flow input 3 (float, m3/h) |  |  |  |
| 125 | QPMIN31 |  |  |  |  |
| 126 | QPMIN32 |  |  |  |  |
| 127 | QPMIN33 |  |  |  |  |
| 128 | QPMIN40 | Min projected value of flow of flow input 4 (float, m3/h) |  |  |  |
| 129 | QPMIN41 |  |  |  |  |
| 130 | QPMIN42 |  |  |  |  |
| 131 | QPMIN43 |  |  |  |  |
| 132 | KTEMP0 | Cold water temperature constant (integer, 0,01 0C) |  |  |  |
| 133 | KTEMP1 |  |  |  |  |
| 134 | (T1-T2)min0 | Min temperature difference T1-T2 (integer, 0,01 0C) |  |  |  |
| 135 | (T1-T2)min1 |  |  |  |  |
| 136 | (T3-T4)min0 | Min temperature difference T3-T4 (integer, 0,01 0C) |  |  |  |
| 137 | (T3-T4)min1 |  |  |  |  |
| 138 | (T1-T2)Pmin0 | Min projekted temperature difference T1-T2 (integer, 0,01 0C) |  |  |  |
| 139 | (T1-T2)Pmin1 |  |  |  |  |
| 140 | (T3-T4)Pmin0 | Min projekted temperature difference T3-T4 (integer, 0,01 0C) |  |  |  |
| 141 | (T3-T4)Pmin1 |  |  |  |  |
| 142 | SIRIB1 | Limits of current of pressure sensor input 1 |  |  | 0x00 – 0-20 mA 0x01 – 4-20 mA 0x02 – 0-4 mA |
| 143 | SIRIB2 | Limits of current of pressure sensor input 2 |  |  |  |
| 144 | SMAX10 | Max value of pressure sensor 1 (integer, 0,1 kPa) |  |  |  |
| 145 | SMAX11 |  |  |  |  |
| 146 | SMAX20 | Max value of pressure sensor 2 (integer, 0,1 kPa) |  |  |  |
| 147 | SMAX21 |  |  |  |  |
| 148 | SENT10 | Value of pressure for calculations for 1st system (integer, 0,1 kPa) |  |  |  |
| 149 | SENT11 |  |  |  |  |
| 150 | SENT20 | Value of pressure for calculations for 2nd system (integer, 0,1 kPa) |  |  |  |
| 151 | SENT21 |  |  |  |  |
| 152 | MBusAddr | M-Bus address |  |  |  |
| 153 | UARTSpeed1 | Boud rate of wire interface | Bits. 7; 6; 5; 4; 3; 2; 1; 0. 0 – None parity 1 – Even parity; 0x00 – 300 bps 0x01 – 600 bps 0x02 – 1200 bps 0x03 – 2400 bps 0x04 – 4800 bps 0x05 – 9600 bps 0x06 – 19200 bps 0x07 – 38400 bps. |
| 154 | UARTSpeed2 | Boud rate of optical interface |  |  |  |
| 155 | DimUnits | Units of energy: 0x00 – MWh 0x01 – Gcal 0x02 - GJ |  |  |  |
| 156 | PKALBA | Report printing language: 0x00 – English 0x01 – Russian 0x02 – Lithuanian |  |  |  |