QALCOSONIC E3

Mbus user protocol

1. General  structure of protocol

  - General features of  protocol

Meter uses a M-bus protocol .

Default  baud rate:   2400 bps,  Even, 1 Stop.

Baud rate can be changed.

Protocol is the same for Mbus interface and for optical interface.

Primmary adress of  Mbus is individual  for Mbus interface and for optical interface.

1.2. Data strings

Data string to meter  SND_NKE:

| 1 | 2 | 3 | 4 | 5 |
| --- | --- | --- | --- | --- |
| 10h | 40h | A | CS | 16h |

A  - M-bus primary address of meter

CS – control sum (the youngest byte of amount of  2-nd and 3-rd  bytes)

Data string to meter  SND_UD2:

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8...n-2 | n-1 | n |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | L | L | 68h | 53h 73h | A | 51h | Data bytes | CS | 16h |

L  - lenght of string (the number of bytes from 5-th to n-2 byte)

A  - M-bus primary address of meter

CS – control sum (the youngest byte of amount of  5-th to n-2  bytes)

Data string to meter  REQ_UD2:

| 1 | 2 | 3 | 4 | 5 |
| --- | --- | --- | --- | --- |
| 10h | 5Bh 7Bh | A | CS | 16h |

A  - M-bus primary address of meter

CS – control sum (the youngest byte of amount of  2-nd and 3-rd  bytes)

Answer of the meter CON:

E5h

Answer of the meter RSP_UD2:

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8...11 | 12, 13 | 14 | 15 | 16 | 17 | 18,19 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | L | L | 68h | C | A | CI | ID | Man | Vrs | Md | TC | St | Sign |

| 20 | ... | ... | ... | ... | ... | ... n-2 | n-1 | n |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DIF | VIF | Data |  | DIF | VIF | Data | CS | 16h |

L  - lenght of string (the number of bytes from 5-th to n-2 byte)

C –   „C field“  (08)

A  - M-bus primary address of meter

CI  - „CI field“

ID – identification number of meter (BSD8, used for secondary addressing, can be changed  - see paragraph 4.1),

Man –   Manufacturer code (AXIOMA Metering UAB  manufacturer code „AXI“:  09h 07h)

Vrs –     number of protocol version (0Bh)

Md –     code of medium (for  „heat / cold energy“:  0Dh)

TC –     counter of telegrams

St   -     meter status code

Sign -   00 00

The bytes  20...n-2  is data from meter:

DIF – code of data format

VIF – code of data units

Data–  values of data

CS – control sum (the youngest byte of amount of  5-th to n-2  bytes).

2. Selection of the data type

## Selection of the data type “All data”

Master sends to the meter  telegram SND_UD2:

| 68h | 03h | 03h | 68h | 53h 73h | A | 50h | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

or

| 68h | 04h | 04h | 68h | 53h 73h | A | 50h | 00h | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Answer of the meter  CON  (if  A not equal FFh):

E5h

## Selection of the data type “User data”

Master sends to the meter  telegram SND_UD2:

| 68h | 04h | 04h | 68h | 53h 73h | A | 50h | 10h | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Answer of the meter  CON  (if  A not equal FFh):

E5h

## Selection of the data type “Simple billing” (Years logger)

Master sends to the meter  telegram SND_UD2:

| 68h | 04h | 04h | 68h | 53h 73h | A | 50h | 20h | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Answer of the meter  CON  (if  A not equal FFh):

E5h

## Selection of the data type “Enhanced billing” (Days logger)

Master sends to the meter  telegram SND_UD2:

| 68h | 04h | 04h | 68h | 53h 73h | A | 50h | 30h | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Answer of the meter  CON  (if  A not equal FFh):

E5h

## Selection of the data type “Multi tariff billing” (Months logger)

Master sends to the meter  telegram SND_UD2:

| 68h | 04h | 04h | 68h | 53h 73h | A | 50h | 40h | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Answer of the meter  CON  (if  A not equal FFh):

E5h

## Selection of the data type “Instantaneous values”

Master sends to the meter  telegram SND_UD2:

| 68h | 04h | 04h | 68h | 53h 73h | A | 50h | 50h | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Answer of the meter  CON  (if  A not equal FFh):

E5h

## Selection of the data type “Load management values for management” (Hours logger)

Master sends to the meter  telegram SND_UD2:

| 68h | 04h | 04h | 68h | 53h 73h | A | 50h | 60h | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Answer of the meter  CON  (if  A not equal FFh):

E5h

## Selection of the data type “Installation and startup”

Master sends to the meter  telegram SND_UD2:

| 68h | 04h | 04h | 68h | 53h 73h | A | 50h | 80h | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Answer of the meter  CON  (if  A not equal FFh):

E5h

## Selection of the data type “Testing”

Master sends to the meter  telegram SND_UD2:

| 68h | 04h | 04h | 68h | 53h 73h | A | 50h | 90h | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Answer of the meter  CON  (if  A not equal FFh):

E5h

## Parameter list for preselecting

If  not satisfied with Default parameter lists (presented in  the tables 1 ... 9). Obtain a desired parameter list presented in Table 11th.

(Paragraph  2.1 ... 2.9) Additionaly it is need to send parameter selecting telegram SND_UD2:

| 68h | L | L | 68h | 53h 73h | A | 51h | SEL1 | SEL2 | … | SELN | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

SEL         selecting parameter code from the table of 11 (made ​​out of sequence as many codes as you want to select of the parameters).

Note . It may be selectes as many parameters but Response telegram length can not exceed 250 bytes.

Answer of the meter  CON  (if  A not equal FFh):

E5h

3. Data request

3.1. Data request

Master sends to the meter  telegram SND_UD2:

| 10h | 5Bh 7Bh | A | CS | 16h |
| --- | --- | --- | --- | --- |

In all cases, except A = FFh, meter response RSP_UD2 telegrame with selected data (tables 1 ...9)

If  no data record, answer of meter is CON:

E5h

3.2. Meter data coding

Table 1

Application reset sub-codes and storages: All data (CI = 50 or  CI = 50 00)

Default list

| # | Parameter | DIF VIF | Type | Units |
| --- | --- | --- | --- | --- |
| 1 | Date and time | 04 6D | 32 bit integer | Type F |
| 2 | Date and time of error starting | 34 6D | 32 bit integer | Type F |
| 3 | Error code | 34 FD 17 | 32 bit integer |  |
| 4 | Battery operation time | 04 20 | 32 bit integer | sec |
| 5 | Working time without error | 04 24 | 32 bit integer | sec |
| 6 | Energy for heating | (04 86 3B) (04 8E 3B) (04 FB 8D 3B) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 7 | Energy for cooling * | (04 86 3C) (04 8E 3C) (04 FB 8D 3C) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 8 | Energy of tariff 1 * | (84 10 86 3x) (84 10 8E 3x) (84 10 FB 8D 3x) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 9 | Energy of tariff 2 * | (84 20 86 3x) (84 20 8E 3x) (84 20 FB 8D 3x) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 10 | Volume | 04 13 | 32 bit integer | 0,001 m3 |
| 11 | Volume of pulse input 1 * | 84 40 13 | 32 bit integer | 0,001 m3 |
| 12 | Volume of pulse input 2 * | 84 80 40 13 | 32 bit integer | 0,001 m3 |
| 13 | Power | 04 2B | 32 bit integer | W |
| 14 | Flow rate | 04 3B | 32 bit integer | 0,001m3/h |
| 15 | Temperature 1 | 02 59 | 16 bit integer | 0,01ºC |
| 16 | Temperature 2 | 02 5D | 16 bit integer | 0,01ºC |
| 17 | Temperature difference | 02 61 | 16 bit integer | 0,01K |
| 18 | Serial number | 0C 78 | 32bit BCD8 |  |
| 19 | CRC | 02 7F | 16 bit integer | CRC16 |

x = B – for energy for heating,  x = C – for energy for cooling

Table 2

Application reset sub-codes and storages: User data (CI = 50 10)

Default list

| # | Parameter | DIF VIF | Type | Units |
| --- | --- | --- | --- | --- |
| 1 | Date and time | 04 6D | 32 bit integer | Type F |
| 2 | Date and time of error starting | 34 6D | 32 bit integer | Type F |
| 3 | Error code | 34 FD 17 | 32 bit integer |  |
| 4 | Battery operation time | 04 20 | 32 bit integer | sec |
| 5 | Volume of pulse input 1 * | 84 40 13 | 32 bit integer | 0,001 m3 |
| 6 | Volume of pulse input 2 * | 84 80 40 13 | 32 bit integer | 0,001 m3 |
| 7 | Pulse value of input 1 * | 02 93 28 | 16 bit integer | 0,001 m3 |
| 8 | Pulse value of input 2 * | 02 93 29 | 16 bit integer | 0,001 m3 |
| 9 | Pulse value of output 1 * | 02 93 2A | 16 bit integer | 0,001 m3 |
| 10 | Pulse value of output 2 * | 02 93 2B | 16 bit integer | 0,001 m3 |
| 11 | Software version | 01 FD 0E | 8 bit integer |  |
| 12 | Yearly set day | 42 EC 7E | Type G |  |
| 13 | Monthly set day | 82 08 EC 7E | Type G |  |
| 14 | Meter type | 0D FD 0B | 88 bit string | “AXI QS E3” |
| 15 | Serial number | 0C 78 | 32bit BCD8 |  |
| 16 | CRC | 02 7F | 16 bit integer | CRC16 |

Table 3

Application reset sub-codes and storages: Simple billing  (Years logger) (CI = 50 20)

Default list

| # | Parameter | DIF VIF | Type | Units |
| --- | --- | --- | --- | --- |
| 1 | Logger date and time | 44 6D | 32 bit integer | Type F |
| 2 | Logger working time without error | 44 24 | 32 bit integer | sec |
| 3 | Logger energy for heating | (44 86 3B) (44 8E 3B) (44 FB 8D 3B) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 4 | Logger energy for cooling * | (44 86 3C) (44 8E 3C) (44 FB 8D 3C) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 5 | Logger energy of tariff 1 * | (C4 10 86 3x) (C4 10 8E 3x) (C4 10 FB 8D 3x) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 6 | Logger energy of tariff 2 * | (C4 20 86 3x) (C4 20 8E 3x) (C4 20 FB 8D 3x) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 7 | Logger volume | 44 13 | 32 bit integer | 0,001 m3 |
| 8 | Logger volume of pulse input 1 * | C4 40 13 | 32 bit integer | 0,001 m3 |
| 9 | Logger volume of pulse input 2 * | C4 80 40 13 | 32 bit integer | 0,001 m3 |
| 10 | CRC | 02 7F | 16 bit integer | CRC16 |

x = B – for energy for heating,  x = C – for energy for cooling

Table 4

Application reset sub-codes and storages: Enhanced billing (Days logger) (CI = 50 30)

Default list

| # | Parameter | DIF VIF | Type | Units |
| --- | --- | --- | --- | --- |
| 1 | Logger date and time | 84 08 6D | 32 bit integer | Type F |
| 2 | Average temperature 1 | 82 08 59 | 16 bit integer | 0,01ºC |
| 3 | Average temperature 2 | 82 08 5D | 16 bit integer | 0,01ºC |
| 4 | Logger working time without error | 84 08 24 | 32 bit integer | sec |
| 5 | Logger energy for heating | (84 08 86 3B) (84 08 8E 3B) (84 08 FB 8D 3B) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 6 | Logger energy for cooling * | (84 08 86 3C) (84 08 8E 3C) (84 08 FB 8D 3C) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 7 | Logger energy of tariff 1 * | (84 18 86 3x) (84 18 8E 3x) (84 18 FB 8D 3x) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 8 | Logger energy of tariff 2 * | (84 28 86 3x) (84 28 8E 3x) (84 28 FB 8D 3x) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 9 | Logger volume | 84 08 13 | 32 bit integer | 0,001 m3 |
| 10 | Logger volume of pulse input 1 * | 84 48 13 | 32 bit integer | 0,001 m3 |
| 11 | Logger volume of pulse input 2 * | 84 88 40 13 | 32 bit integer | 0,001 m3 |
| 12 | Logger duration when q > qmax | 84 08 BB 58 | 32 bit integer | sec |
| 13 | CRC | 02 7F | 16 bit integer | CRC16 |

x = B – for energy for heating,  x = C – for energy for cooling

Table 5

Application reset sub-codes and storages: Multi tariff billing (Months logger) (CI = 50 40)

Default list

| # | Parameter | DIF VIF | Type | Units |
| --- | --- | --- | --- | --- |
| 1 | Logger date and time | 84 08 6D | 32 bit integer | Type F |
| 2 | Average temperature 1 | 82 08 59 | 16 bit integer | 0,01ºC |
| 3 | Average temperature 2 | 82 08 5D | 16 bit integer | 0,01ºC |
| 4 | Logger working time without error | 84 08 24 | 32 bit integer | sec |
| 5 | Logger energy for heating | (84 08 86 3B) (84 08 8E 3B) (84 08 FB 8D 3B) | 32 bit integer | kWh (MJ) (Mcal) |
| 6 | Logger energy for cooling * | (84 08 86 3C) (84 08 8E 3C) (84 08 FB 8D 3C) | 32 bit integer | kWh (MJ) (Mcal) |
| 7 | Logger energy of tariff 1 * | (84 18 86 3x) (84 18 8E 3x) (84 18 FB 8D 3x) | 32 bit integer | kWh (MJ) (Mcal) |
| 8 | Logger energy of tariff 2 * | (84 28 86 3x) (84 28 8E 3x) (84 28 FB 8D 3x) | 32 bit integer | kWh (MJ) (Mcal) |
| 9 | Logger volume | 84 08 13 | 32 bit integer | 0,001 m3 |
| 10 | Logger volume of pulse input 1 * | 84 48 13 | 32 bit integer | 0,001 m3 |
| 11 | Logger volume of pulse input 2 * | 84 88 40 13 | 32 bit integer | 0,001 m3 |
| 12 | Logger duration when q > qmax | 84 08 BE 58 | 32 bit integer | sec |
| 13 | CRC | 02 7F | 16 bit integer | CRC16 |

x = B – for energy for heating,  x = C – for energy for cooling

Remark.

If meter is  specialy configured, in table 5 listed monthly parameters data is transmitted and in accordance after  inquiry (“All data” table 1) data transmission.

Table 6

Application reset sub-codes and storages: Instantaneous values (CI = 50 50)

Default list

| # | Parameter | DIF VIF | Type | Units |
| --- | --- | --- | --- | --- |
| 1 | Date and time | 04 6D | 32 bit integer | Type F |
| 2 | Date and time of error starting | 34 6D | 32 bit integer | Type F |
| 3 | Error code | 34 FD 17 | 32 bit integer |  |
| 4 | Battery operation time | 04 20 | 32 bit integer | sec |
| 5 | Working time without error | 04 24 | 32 bit integer | sec |
| 6 | Energy for heating | (04 86 3B) (04 8E 3B) (04 FB 8D 3B) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 7 | Energy for cooling * | (04 86 3C) (04 8E 3C) (04 FB 8D 3C) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 8 | Energy of tariff 1 * | (84 10 86 3x) (84 10 8E 3x) (84 10 FB 8D 3x) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 9 | Energy of tariff 2 * | (84 20 86 3x) (84 20 8E 3x) (84 20 FB 8D 3x) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 10 | Volume | 04 13 | 32 bit integer | 0,001 m3 |
| 11 | Volume of pulse input 1 * | 84 40 13 | 32 bit integer | 0,001 m3 |
| 12 | Volume of pulse input 2 * | 84 80 40 13 | 32 bit integer | 0,001 m3 |
| 13 | Power | 04 2B | 32 bit integer | W |
| 14 | Flow rate | 04 3B | 32 bit integer | 0,001m3/h |
| 15 | Temperature 1 | 02 59 | 16 bit integer | 0,01ºC |
| 16 | Temperature 2 | 02 5D | 16 bit integer | 0,01ºC |
| 17 | Temperature difference | 02 61 | 16 bit integer | 0,01K |
| 18 | Meter type | 0D FD 0B | 88 bit string | “AXI QS E3” |
| 19 | Serial number | 0C 78 | 32bit BCD8 |  |
| 20 | CRC | 02 7F | 16 bit integer | CRC16 |

x = B – for energy for heating,  x = C – for energy for cooling

Table 7

Application reset sub-codes and storages: Load management values for management

(Hours logger)  (CI = 50 60)     Default list

| # | Parameter | DIF VIF | Type | Units |
| --- | --- | --- | --- | --- |
| 1 | Logger date and time | C4 86 03 6D | 32 bit integer | Type F |
| 2 | Average power | C4 86 03 2B | 32 bit integer | W |
| 3 | Average flow | C4 86 03 3B | 32 bit integer | 0,001m3/h |
| 4 | Average temperature 1 | C2 86 03 59 | 16 bit integer | 0,01ºC |
| 5 | Average temperature 2 | C2 86 03 5D | 16 bit integer | 0,01ºC |
| 6 | Logger min flow | E4 86 03 3B | 32 bit integer | 0,001m3/h |
| 7 | Logger max flow | D4 86 03 3B | 32 bit integer | 0,001m3/h |
| 8 | Logger min temperature difference | E2 86 03 61 | 16 bit integer | 0,01K |
| 9 | Logger max temperature difference | D2 86 03 61 | 16 bit integer | 0,01K |
| 10 | Logger error code | F4 86 03 FD 17 | 32 bit integer |  |
| 11 | Logger working time without error | C4 86 03 24 | 32 bit integer | sec |
| 12 | Logger energy for heating | (C4 86 03 86 3B) (C4 86 03 8E 3B) (C4 86 03 FB 8D 3B) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 13 | Logger energy for cooling * | (C4 86 03 86 3C) (C4 86 03 8E 3C) (C4 86 03 FB 8D 3C) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 14 | Logger energy of tariff 1 * | (C4 96 03 86 3x) (C4 96 03 8E 3x) (C4 96 03 FB 8D 3x) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 15 | Logger energy of tariff 2 * | (C4 A6 03 86 3x) (C4 A6 03 8E 3x) (C4 A6 03 FB 8D 3x) | 32 bit integer | (kWh), (MJ), (Mcal). |
| 16 | Logger volume | C4 86 03 13 | 32 bit integer | 0,001 m3 |
| 17 | Logger volume of pulse input 1 * | C4 C6 03 13 | 32 bit integer | 0,001 m3 |
| 18 | Logger volume of pulse input 2 * | C4 86 43 13 | 32 bit integer | 0,001 m3 |
| 19 | Logger duration when q > qmax | C4 86 03 BE 58 | 32 bit integer | sec |
| 20 | CRC | 02 7F | 16 bit integer | CRC16 |

x = B – for energy for heating,  x = C – for energy for cooling

Table 8

Application reset sub-codes and storages: Installation and startup  (CI = 50 80)

Default list

| # | Parameter | DIF VIF | Type | Units |
| --- | --- | --- | --- | --- |
| 1 | Date and time | 04 6D | 32 bit integer | Type F |
| 2 | Date and time of error starting | 34 6D | 32 bit integer | Type F |
| 3 | Error code | 34 FD 17 | 32 bit integer |  |
| 4 | Battery operation time | 04 20 | 32 bit integer | sec |
| 5 | Working time without error | 04 24 | 32 bit integer | sec |
| 6 | Test mode status | 01 FF 03 | 8 bit integer |  |
| 7 | Device mode status | 01 FF 04 | 8 bit integer |  |
| 8 | Software version | 01 FD 0E | 8 bit integer |  |
| 9 | Yearly set day | 42 EC 7E | Type G |  |
| 10 | Monthly set day | 82 08 EC 7E | Type G |  |
| 11 | Meter type | 0D FD 0B | 88 bit string | “AXI QS E3” |
| 12 | Serial number | 0C 78 | 32bit BCD8 |  |
| 13 | CRC | 02 7F | 16 bit integer | CRC16 |

Table 9

Application reset sub-codes and storages: Testing (CI = 50 90)

Default list

| # | Parameter | DIF VIF | Type | Units |
| --- | --- | --- | --- | --- |
| 1 | Date and time | 04 6D | 32 bit integer | Type F |
| 2 | Date and time of error starting | 34 6D | 32 bit integer | Type F |
| 3 | Error code | 34 FD 17 | 32 bit integer |  |
| 4 | Battery operation time | 04 20 | 32 bit integer | sec |
| 5 | Flow rate | 04 3B | 32 bit integer | 0,001m3/h |
| 6 | Temperature 1 | 02 59 | 16 bit integer | 0,01ºC |
| 7 | Temperature 2 | 02 5D | 16 bit integer | 0,01ºC |
| 8 | Temperature difference | 02 61 | 16 bit integer | 0,01K |
| 9 | Pulse value of energy test output | 02 FF 01 | 16 bit integer |  |
| 10 | Pulse value of volume test output | 02 FF 02 | 16 bit integer |  |
| 11 | Test mode status | 01 FF 03 | 8 bit integer |  |
| 12 | Device mode status | 01 FF 04 | 8 bit integer |  |
| 13 | Volume high resolution | 04 01 | 32 bit integer | mWh |
| 14 | Energy high resolution | 04 10 | 32 bit integer | ml |
| 15 | Device configuration | 01 FF 09 | 8 bit integer |  |
| 16 | Software version | 01 FD 0E | 8 bit integer |  |
| 17 | Device type | 0D FD 0B | 88 bit string | “AXI QS E3” |
| 18 | Seial number | 0C 78 | 32bit BCD8 |  |
| 19 | CRC | 02 7F | 16 bit integer | CRC16 |

Table 10

Error code encryption

| Byte N | Bite N | if bite = 1 | LCD indication code “ERROR xxxx” |
| --- | --- | --- | --- |
|  | 0 | - |  |
|  | 1 | - |  |
|  | 2 | Hardware status flag Er02 | 8000 |
| 0 | 3 | Hardware status flag Er03 | 8000 |
|  | 4 | End of battery live time | 1000 |
|  | 5 | Hardware status flag Er05 | 0008 |
|  | 6 | - |  |
|  | 7 | - |  |
|  | 0 | - |  |
|  | 1 | - |  |
|  | 2 | Flow sensor is empty | 0001 |
| 1 | 3 | Flow flows in a reverse direction | 0002 |
|  | 4 | Flow rate less qi |  |
|  | 5 | - |  |
|  | 6 | - |  |
|  | 7 | - |  |
|  | 0 | Temperture sensor 1 error or short circuit | 0080 |
|  | 1 | Temperture sensor 1 disconected | 0080 |
|  | 2 | Temperture 1 < 0ºC | 00C0 |
| 2 | 3 | Temperture 1 > 180ºC | 0080 |
|  | 4 | Temperture sensor2 error or short circuit | 0800 |
|  | 5 | Temperture sensor 2 disconected | 0800 |
|  | 6 | Temperture 2 < 0ºC | 0C00 |
|  | 7 | Temperture 2 > 180ºC | 0800 |
|  | 0 | Hardware status flag Er30 | 0880 |
|  | 1 | - |  |
|  | 2 | Temperature difference < 3ºC | 4000 |
| 3 | 3 | Temperature difference > 150ºC | 2000 |
|  | 4 | Flow rate greater 1,2qs | 0004 |
|  | 5 | Hardware status flag Er35 | 8000 |
|  | 6 | - |  |
|  | 7 | Hardware status flag Er37 | 8000 |

Table 11

Parameters list for preselecting

| DIF VIF |
| --- |
| # | Parameter | SEL | CI = 50 Instantaneous | CI = 50 60 Hours logger | CI = 50 30 Days logger | CI = 50 40 Months logger | CI = 50 20 Years logger | Type | Units |
| 1 | Date and time stamp | C8 FF 7F 6D | 04 6D | C4 86 03 6D | 84 08 6D | 84 08 6D | 44 6D | 32 bit integer | Type F |
| 2 | Working time without error | C8 FF 7F 24 | 04 24 | C4 86 03 24 | 84 08 24 | 84 08 24 | 44 24 | 32 bit integer | sec |
| 3 | Error code | F8 FF 7F FD 17 | 34 FD 17 | F4 86 03 FD 17 | B4 08 FD 17 | B4 08 FD 17 | 74 FD 17 | 32 bit integer |  |
| 4 | Date and time of error starting | F8 FF 7F 6D | 34 6D | - | - | - | - | 32 bit integer | Type F |
| 5 | Energy for heating | C8 0F FE 3B ( C8 0F FE FE 3B for „Mcal“ ) | (04 86 3B) (04 8E 3B) (04 FB 8D 3B) | (C4 86 03 86 3B) (C4 86 03 8E 3B) (C4 86 03 FB 8D 3B) | (84 08 86 3B) (84 08 8E 3B) (84 08 FB 8D 3B) | (84 08 86 3B) (84 08 8E 3B) (84 08 FB 8D 3B) | (44 86 3B) (44 8E 3B) (44 FB 8D 3B) | 32 bit integer | kWh (MJ) (Mcal) |
| 6 | Energy for cooling * | C7 0F FE 3C ( C8 0F FE FE 3C for „Mcal“ ) | (04 86 3C) (04 8E 3C) (04 FB 8D 3C) | (C4 86 03 86 3C) (C4 86 03 8E 3C) (C4 86 03 FB 8D 3C) | (84 08 86 3C) (84 08 8E 3C) (84 08 FB 8D 3C) | (84 08 86 3C) (84 08 8E 3C) (84 08 FB 8D 3C) | (44 86 3C) (44 8E 3C) (44 FB 8D 3C) | 32 bit integer | kWh (MJ) (Mcal) |
| 7 | Volume | C8 FF 7F 13 | 04 13 | C4 86 03 13 | 84 08 13 | 84 08 13 | 44 13 | 32 bit integer | 0,001m3 |
| 8 | Energy of tariff 1 * | C8 1F 7E | (84 10 86 3x) (84 10 8E 3x) (84 10 FB 8D 3x) | (C4 96 03 86 3x) (C4 96 03 8E 3x) (C4 96 03 FB 8D 3x) | (84 18 86 3x) (84 18 8E 3x) (84 18 FB 8D 3x) | (84 18 86 3x) (84 18 8E 3x) (84 18 FB 8D 3x) | (C4 10 86 3x) (C4 10 8E 3x) (C4 10 FB 8D 3x) | 32 bit integer | kWh (MJ) (Mcal) |
| 9 | Energy of tariff 2 * | C8 BF 7F 7E | (84 20 86 3x) (84 20 8E 3x) (84 20 FB 8D 3x) | (C4 A6 03 86 3x) (C4 A6 03 8E 3x) (C4 A6 03 FB 8D 3x) | (84 28 86 3x) (84 28 8E 3x) (84 28 FB 8D 3x) | (84 28 86 3x) (84 28 8E 3x) (84 28 FB 8D 3x) | (C4 20 86 3x) (C4 20 8E 3x) (C4 20 FB 8D 3x) | 32 bit integer | kWh (MJ) (Mcal) |
| 10 | Volume of pulse input 1 * | C8 FF 3F 7B | 84 40 13 | C4 C6 03 13 | 84 48 13 | 84 48 13 | C4 40 13 | 32 bit integer | 0,001 m3 |
| 11 | Volume of pulse input 2 * | C8 BF 7F 7B | 84 80 40 13 | C4 86 43 13 | 84 88 40 13 | 84 88 40 13 | C4 80 40 13 | 32 bit integer | 0,001 m3 |
| 12 | Average power | C8 FF 7F 2B | 04 2B | C4 86 03 2B | 84 08 2B | 84 08 2B | 44 2B | 32 bit integer | W |
| 13 | Averago Flow rate | C8 FF 7F 3B | 04 3B | C4 86 03 3B | 84 08 3B | 84 08 3B | 44 3B | 32 bit integer | 0,001m3/h |
| 14 | Average Temperature 1 | C8 FF 7F 59 | 02 59 | C2 86 03 59 | 82 08 59 | 82 08 59 | 42 59 | 16 bit integer | 0,01ºC |
| 15 | Average Temperature 2 | C8 FF 7F 5D | 02 5D | C2 86 03 5D | 82 08 5D | 82 08 5D | 42 5D | 16 bit integer | 0,01ºC |
| 16 | Average Temperature difference | C8 FF 7F 61 | 02 61 | C2 86 03 61 | 82 08 61 | 82 08 61 | 42 61 | 16 bit integer | 0,01K |
| 17 | Min Power | E8 FF 7F 2B | - | E4 86 03 2B | A4 08 2B | A4 08 2B | 64 2B | 32 bit integer | W |
| 18 | Min Power date | E8 FF 7F AB 6D | - | E4 86 03 AB 6D | A4 08 AB 6D | A4 08 AB 6D | 64 AB 6D | 32 bit integer | Type F |
| 19 | Max Power | D8 FF 7F 2B | - | D4 86 03 2B | 94 08 2B | 94 08 2B | 54 2B | 32 bit integer | W |
| 20 | Max Power date | D8 FF 7F AB 6D | - | D4 86 03 AB 6D | 94 08 AB 6D | 94 08 AB 6D | 54 AB 6D | 32 bit integer | Type F |
| 21 | Min Flow rate | E8 FF 7F 3B | - | E4 86 03 3B | A4 08 3B | A4 08 3B | 64 3B | 32 bit integer | 0,001m3/h |
| 22 | Min Flow rate Date | E8 FF 7F BB 6D | - | E4 86 03 BB 6D | A4 08 BB 6D | A4 08 BB 6D | 64 BB 6D | 32 bit integer | Type F |
| 23 | Max Flow rate | D8 FF 7F 3B | - | D4 86 03 3B | 94 08 3B | 94 08 3B | 54 3B | 32 bit integer | 0,001m3/h |
| 24 | Max Flow rate Date | D8 FF 7F BB 6D | - | D4 86 03 BB 6D | 94 08 BB 6D | 94 08 BB 6D | 54 BB 6D | 32 bit integer | Type F |
| 25 | Min Temerature 1 | E8 FF 7F DB 59 | - | E2 86 03 59 | A2 08 59 | A4 08 59 | 62 59 | 16 bit integer | 0,01ºC |
| DIF VIF |
| # | Parameter | SEL | CI = 50 Instantaneous | CI = 50 60 Hours logger | CI = 50 30 Days logger | CI = 50 40 Months logger | CI = 50 20 Years logger | Type | Units |
| 26 | Min Temerature 1 Date | E8 FF 7F D9 6D | - | E4 86 03 D9 6D | A4 08 D9 6D | A4 08 D9 6D | 64 D9 6D | 32 bit integer | Type F |
| 27 | Max Temperature 1 | D8 FF 7F 59 | - | D2 86 03 59 | 92 08 59 | 92 08 59 | 52 59 | 16 bit integer | 0,01ºC |
| 28 | Max Temperature 1 Date | D8 FF 7F D9 6D | - | D4 86 03 D9 6D | 94 08 D9 6D | 94 08 D9 6D | 54 D9 6D | 32 bit integer | Type F |
| 29 | Min temperature 2 | E8 FF 7F 5D | - | E2 86 03 5D | A2 08 5D | A2 08 5D | 62 5D | 16 bit integer | 0,01ºC |
| 30 | Min Temperature 2 Date | E8 FF 7F DD 6D | - | E4 86 03 DD 6D | A4 08 DD 6D | A4 08 DD 6D | 64 DD 6D | 32 bit integer | Type F |
| 31 | Max Temperature 2 | D8 FF 7F 5D | - | D2 86 03 5D | 92 08 5D | 92 08 5D | 52 5D | 16 bit integer | 0,01ºC |
| 32 | Max Temperature 2 Date | D8 FF 7F DD 6D | - | D4 86 03 DD 6D | 94 08 DD 6D | 94 08 DD 6D | 54 DD 6D | 32 bit integer | Type F |
| 33 | Min Temperature difference | E8 FF 7F 61 | - | E2 86 03 61 | A2 08 61 | A2 08 61 | 62 61 | 16 bit integer | 0,01K |
| 34 | Min Temperature difference Date | E8 FF 7F E1 6D | - | E4 86 03 E1 6D | A4 08 E1 6D | A4 08 E1 6D | 64 E1 6D | 32 bit integer | Type F |
| 35 | Max Temperature difference | D8 FF 7F 61 | - | D2 86 03 61 | 92 08 61 | 92 08 61 | 52 61 | 16 bit integer | 0,01K |
| 36 | Max Temperature difference Date | D8 FF 7F E1 6D | - | D4 86 03 E1 6D | 94 08 E1 6D | 94 08 E1 6D | 54 E1 6D | 32 bit integer | Type F |
| 37 | Duration when q < qmin | C8 FF 7F BE 50 | 04 BE 50 | C4 86 03 BE 50 | 84 08 BE 50 | 84 08 BE 50 | 44 BE 50 | 32 bit integer | sec |
| 38 | Flow min level qmin | C8 FF 7F BE 40 | 05 BE 40 | - | - | - | - | float | 1 m3/h |
| 39 | Duration when q > qmax | C8 FF 7F BE 58 | 04 BE 58 | C4 86 03 BE 58 | 84 08 BE 58 | 84 08 BE 58 | 44 BE 58 | 32 bit integer | sec |
| 40 | Flow max level qmax | C8 FF 7F BE 48 | 05 BE 48 | - | - | - | - | float | 1 m3/h |
| 41 | Battery operation time | C8 FF 7F 20 | 04 20 | - | - | - | - | 32 bit integer | sec |
| 42 | Energy high resolution | C8 FF 7F 01 | 04 01 | - | - | - | - | 32 bit integer |  |
| 43 | Volume high resolution | C8 FF 7F 10 | 04 10 | - | - | - | - | 32 bit integer |  |

x = B – for energy for heating,  x = C – for energy for cooling

Remarks.

- Table 1…11 energy and volume  DIF VIF codes are provided of comma position for 0,001 MWh, 0,001 GJ, 0,001 Gcal and  0,001 m3.  Other values ​​can be set for the energy and volume.

- Table 1…11 parameters marked  “*”,  will be transmitted only if the conditions  are kept:

Table 12

| Parameter | Condition |
| --- | --- |
| Energy for cooling . Logger energy for cooling | Heat meter application type – for measurement of energy consumed for heating and cooling |
| Energy of tariff 1. Logger energy of tariff 1 | Tariff 1 function is On |
| Energy of tariff 2, Logger energy of tariff 2 | Tariff 2 function is On |
| Volume of pulse input 1, Logger pulse input 1 | Pulse input 1 is active |
| Volume of pulse input 2, Logger pulse input 2 | Pulse input 2 is active |
| Pulse value of output 1 | Pulse output 1 is active |
| Pulse value of output 2 | Pulse output 2 is active |

## 3.3. CRC16 checksum  calculation algorithm

/*

* The polynomial x^0 + x^5 + x^12.

*/

const __u16 crc_ccitt_table[256] = {

0x0000, 0x1189, 0x2312, 0x329b, 0x4624, 0x57ad, 0x6536, 0x74bf,

0x8c48, 0x9dc1, 0xaf5a, 0xbed3, 0xca6c, 0xdbe5, 0xe97e, 0xf8f7,

0x1081, 0x0108, 0x3393, 0x221a, 0x56a5, 0x472c, 0x75b7, 0x643e,

0x9cc9, 0x8d40, 0xbfdb, 0xae52, 0xdaed, 0xcb64, 0xf9ff, 0xe876,

0x2102, 0x308b, 0x0210, 0x1399, 0x6726, 0x76af, 0x4434, 0x55bd,

0xad4a, 0xbcc3, 0x8e58, 0x9fd1, 0xeb6e, 0xfae7, 0xc87c, 0xd9f5,

0x3183, 0x200a, 0x1291, 0x0318, 0x77a7, 0x662e, 0x54b5, 0x453c,

0xbdcb, 0xac42, 0x9ed9, 0x8f50, 0xfbef, 0xea66, 0xd8fd, 0xc974,

0x4204, 0x538d, 0x6116, 0x709f, 0x0420, 0x15a9, 0x2732, 0x36bb,

0xce4c, 0xdfc5, 0xed5e, 0xfcd7, 0x8868, 0x99e1, 0xab7a, 0xbaf3,

0x5285, 0x430c, 0x7197, 0x601e, 0x14a1, 0x0528, 0x37b3, 0x263a,

0xdecd, 0xcf44, 0xfddf, 0xec56, 0x98e9, 0x8960, 0xbbfb, 0xaa72,

0x6306, 0x728f, 0x4014, 0x519d, 0x2522, 0x34ab, 0x0630, 0x17b9,

0xef4e, 0xfec7, 0xcc5c, 0xddd5, 0xa96a, 0xb8e3, 0x8a78, 0x9bf1,

0x7387, 0x620e, 0x5095, 0x411c, 0x35a3, 0x242a, 0x16b1, 0x0738,

0xffcf, 0xee46, 0xdcdd, 0xcd54, 0xb9eb, 0xa862, 0x9af9, 0x8b70,

0x8408, 0x9581, 0xa71a, 0xb693, 0xc22c, 0xd3a5, 0xe13e, 0xf0b7,

0x0840, 0x19c9, 0x2b52, 0x3adb, 0x4e64, 0x5fed, 0x6d76, 0x7cff,

0x9489, 0x8500, 0xb79b, 0xa612, 0xd2ad, 0xc324, 0xf1bf, 0xe036,

0x18c1, 0x0948, 0x3bd3, 0x2a5a, 0x5ee5, 0x4f6c, 0x7df7, 0x6c7e,

0xa50a, 0xb483, 0x8618, 0x9791, 0xe32e, 0xf2a7, 0xc03c, 0xd1b5,

0x2942, 0x38cb, 0x0a50, 0x1bd9, 0x6f66, 0x7eef, 0x4c74, 0x5dfd,

0xb58b, 0xa402, 0x9699, 0x8710, 0xf3af, 0xe226, 0xd0bd, 0xc134,

0x39c3, 0x284a, 0x1ad1, 0x0b58, 0x7fe7, 0x6e6e, 0x5cf5, 0x4d7c,

0xc60c, 0xd785, 0xe51e, 0xf497, 0x8028, 0x91a1, 0xa33a, 0xb2b3,

0x4a44, 0x5bcd, 0x6956, 0x78df, 0x0c60, 0x1de9, 0x2f72, 0x3efb,

0xd68d, 0xc704, 0xf59f, 0xe416, 0x90a9, 0x8120, 0xb3bb, 0xa232,

0x5ac5, 0x4b4c, 0x79d7, 0x685e, 0x1ce1, 0x0d68, 0x3ff3, 0x2e7a,

0xe70e, 0xf687, 0xc41c, 0xd595, 0xa12a, 0xb0a3, 0x8238, 0x93b1,

0x6b46, 0x7acf, 0x4854, 0x59dd, 0x2d62, 0x3ceb, 0x0e70, 0x1ff9,

0xf78f, 0xe606, 0xd49d, 0xc514, 0xb1ab, 0xa022, 0x92b9, 0x8330,

0x7bc7, 0x6a4e, 0x58d5, 0x495c, 0x3de3, 0x2c6a, 0x1ef1, 0x0f78

};

/*

*	crc_ccitt - recompute the CRC for the data buffer

*	@crc - previous CRC value

*	@buffer - data pointer

*	@len - number of bytes in the buffer

*/

__u16 crc_ccitt(__u16 crc, __u8 const *buffer, size_t len)

{

while (len--)

crc = (crc >> 8) ^ crc_ccitt_table[(crc ^ (*buffer++)) & 0xff];

return crc;

}

4. Settings the parameters of meter

### 4.1. Changing  the identification number

Master sends to the meter  string  SND_UD2 with new  identification number „ID“ (BCD8 format):

| 68h | 09h | 09h | 68h | 53h 73h | A | 51h | 0Ch | 79h | ID | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Answer of the meter  CON  (if  A not equal FFh):

E5h

### 4.2. Changing  the identification number, Manufacturer ID and Medium

Master sends to the meter  string  SND_UD2 with new  Complete  ID  (64 bit integer):

| 68h | 0Dh | 0Dh | 68h | 53h 73h | A | 51h | 07h | 79h | Complete ID (64 bit) | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Answer of the meter  CON  (if  A not equal FFh):

E5h

Structure of  “Complete  ID”  (64 bit integer):

| Identification number „ID“ | Manufacturer ID | Generation | Medium |
| --- | --- | --- | --- |
| 4 byte (BCD8 format) | 2 byte | 1 byte | 1 byte |

### Remark: Generation code is ignored (In meter Generation code is fixed 0Bh)

### 4.3. Changing  the primary address

Master sends to the meter  string  SND_UD2 with new  primary address „aa“:

| 68h | 06h | 06h | 68h | 53h 73h | A | 51h | 01h | 7Ah | aa | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Answer of the meter  CON  (if  A not equal FFh):

E5h

### 4.4. Changing the data and time of the meter

Master sends to the meter  string  SND_UD2 with new  data and time:

| 68h | 09h | 09h | 68h | 53h 73h | A | 51h | 04h | 6Dh | Dat and time (Type F) | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Answer of the meter  CON  (if  A not equal FFh):

E5h

### 4.5. Changing the yearly set day

Master sends to the meter  string  SND_UD2 with new  set data :

| 68h | 08h | 08h | 68h | 53h 73h | A | 51h | 42h | ECh | 7Eh | Month and day (Type G) | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Answer of the meter  CON  (if  A not equal FFh):

E5h

### 4.6. Changing the monthly set day

Master sends to the meter  string  SND_UD2 with new  set data :

| 68h | 09h | 09h | 68h | 53h 73h | A | 51h | 82h | 08h | ECh | 7Eh | Day (Type G) | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Answer of the meter  CON  (if  A not equal FFh):

E5h

Remark. Changig the identification number and the set date is possible only when meter is set to SERVICE mode.

### 4.7. Changing the baud rate

Master sends to the meter  string  SND_UD2 with new  baud rate code „BR“:

| 68h | 03h | 03h | 68h | 53h 73h | A | BR | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Answer of the meter  CON  (if  A not equal FFh) with old baud rate:

E5h

Values of  BR code:

BR=B8h –  for changing boud rate to 300 bps

BR=B9h –  for changing boud rate to 600 bps

BR=BAh – for changing boud rate to 1200 bps

BR=BBh – for changing boud rate to 2400 bps

BR=BCh – for changing boud rate to 4800 bps

BR=BDh – for changing boud rate to 9600 bps

5. Secondary addressing

  - Selecting of the meter

Master sends to the meter  string  SND_UD2 :

| 68h | 0Bh | 0Bh | 68h | 53h 73h | FD | 52 | NN | NN | NN | NN | HH | HH | ID | MM | CS | 16h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

NN –  Identification number (secondary adress)  BCD8 format       (if „F“-  this number ignored)

HH –   Manufacturer code,  HST format                                         (if „FF“-  this byte ignored)

ID –    Identification code,  HST format                                          (if „FF“-  ignored)

MM – Medium code, SMED format                                               (if „FF“-  ignored)

The meter, whose identification number is the same, is selected for further communication and send answer  CON:

E5h

  - Communication with selected meter

Communication with selected meter carried out as usual:

- data type for reading is selected by sending to meter strig SND_UD2 (see paragraph 2), only in this case, M-bus adress must be  FDh,

- answer of the selected meter  CON  :

E5h

- for data request master sends to the meter  string (M-bus adress must be  FDh):

| 10h | 5Bh 7Bh | FDh | CS | 16h |
| --- | --- | --- | --- | --- |

- meter response RSP_UD2 telegrame with selected data (tables 1 ...9)

  - Deselection of seccondary addresing mode

Master sends to the meter  telegram  SND_NKE with  adress FDh :

| 10h | 40h | FDh | CS | 16h |
| --- | --- | --- | --- | --- |